## DG Checklist
DG DAILY CHECK LIST
Month: |  | DG NO: | [8 empty] | Capacity: | [6 empty] | Location:-
Sl.No | Checks | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Put the DG set in manual mode
2 | Check the diesel level in the diesel tank,Ensure it is above 800ltrs
3 | Check the lube oil level and top up if required | [31 empty] | TAS/FMD/ENG/03/R0
4 | Check the coolant level in the radiator,top up if required
5 | Check level of battery distilled water,specific gravity and cleanliness of terminals.
6 | Note down the Battery Voltage
7 | Check the terminals and applied petroleum jelly
8 | Ensure all the drive belts are tight
9 | Ensure no leakage in fuel,oil,water and exhaust line
10 | Ensure cleanliness of equipment and surrounding area
11 | Check operation of AMF panel
12 | Test run the DG sets for 5 minutes and note down the parameter in DG log book
13 | Put the DG set in Auto mode
14 | Check the proper working condition of DG panel in LT room
Signature Of DG Tech
Signature Of Supervisor
Date | Abnormalities |  |  |  | Action Taken | [13 empty] | Status |  |  |  |  | Remarks
Signature of Team Leader | [24 empty] | Signature of Manager

## Chiller pump checklist
DAILY OPERATIONAL CHECK LIST FOR CHILLER PUMP
EQUIPMENT NO. |  | LOCATION:- | [23 empty] | MONTH:-
SL. No | Description | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Check for any abnormal noise & vibration while running.
2 | Check for gland water leakage at the pump end. (Allowable less than 60 drops/min)
3 | Log Pump discharge pressure, (Range: 1.5 to 3 Kg/Sqcm)
4 | Check the tightness of base foundation bolts by paint match marking.
5 | Check for abnormal heat in motor and correct if so.
6 | Ensure cleanliness of Pump and free from cobweb.
7 | Enure cleanliness of pipelines with Aluminium clading insulation up to 6 feet and free from cobweb
Technicain Sign
Supervisor Sign
DATE | ABNORMALITY | LOCATION:- 22: ACTION TAKEN; MONTH:- 27: STATUS; MONTH:- 29: SIGNATURE
Signature of Team Leader |  | LOCATION:- 24: Signature of Manager
.
0
0

## RMU Yard Check List
Daily checklist for RMU Yard
Month: | [17 empty] | Location:
Sl.No | Checks | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Visually inspect all equipment for any abnormality, over heating etc
2 | Visually inspect all cables for fraying and discolor due to heating.
3 | Check the functionality of all the meters
4 | Note down all the readings of the meter
5 | Check the condition of the breakers
6 | Ensure yard is cleaned
Signature Of Elect Tech
Signature Of Supervisor
Date Time | Abnormalities |  |  |  | Action Taken | [13 empty] | Status |  |  |  |  | Remarks
Signature Of Team Leader | [24 empty] | Signature of Manager

## Transformer
Daily checklist for Transformer
Month: |  | KVA:- | [15 empty] | Location:-
Sl.No | Checks | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Check the transformer Oil level
2 | Check for any leakage from transformers
3 | Visually inspect all equipment for for any abnormality, over heating etc | [31 empty] | TAS/FMD/ENG/05/R0
4 | Log the transformer oil temperature
5 | Log the transformer winding temperature
6 | Check the OLTC tap position
7 | Check the condition of silica gel in breather
8 | Ensure yard is cleaned
Signature of Elect Tech
Signature of Supervisor
Date Time | Abnormalities |  |  |  | Action Taken | [13 empty] | Status |  |  |  |  | Remarks
Signature Of Team Leader | [23 empty] | Signature of Manager

## LT Panels
Daily checklist for LT panels
Month: | [17 empty] | Location:
Sl.No | Checks | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Ensure the LT panel is cleaned
2 | Check for any fault indication
3 | Check for any overheating of all CB's
4 | Ensure the LT panel room is cleaned
5 | Check the room temp and switch ON the exhaust fan if required
6 | Check sevicability of all the meters
7 | Check the earthing terminals
8 | Ensure the electric insulated mats are clean and arranged properly
9 | check the cable ends whether getting blackening
10 | Check the cable whether getting heating
11 | Note down all parameters from the panels
Signature of Elect Tech
Signature of Supervisor
Date | Abnormalities |  |  |  | Action Taken | [13 empty] | Status |  |  |  |  | Remarks
Signature Of Team Leader | [23 empty] | Signature of Manager

## Lift
DAILY CHECK LIST FOR LIFT
Month: |  | LIFT NO: | [6 empty] | Capacity: | [6 empty] | Location:
S.No | NAME |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Cleanlines of the car
2 | Check all the buttons in the car
3 | Check the the bulb and fan in the car is working
4 | check the landing of the car in every floor for proper floor level
5 | check all the car calling buttons and bulbs for proper functioning | [32 empty] | TAS/FMD/ENG/07/R0
6 | Ensure the cleanlines of the lift room
7 | Ensure the sensor for the proper functioning without any extra time delay
8 | Check the lift panel for any fault indications
9 | Check the motor of the lift for any abnormal sound
10 | Check the cleanlines of both the lift panel and motor
11 | check the working of telephones
Signature of tech
Signature Of Supervisor
Date Time | Abnormalities |  | 1: Action Taken; Location: 15: Status; Location: 20: Remarks
Signature Of Team Leader |  |  | Location: 22: Signature of Manager

## FFS
FIRE FIGHTING DAILY CHECK LIST
Month: |  | DG NO: | [8 empty] | Capacity: | [6 empty] | Location:
Sl. No | Checks | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Put the pump in manual mode
2 | Check the diesel level in the Diesel tank and ensure it is 200 lts
3 | Check lube oil and top up if required
4 | Check coolant level in radiator, top up if required
5 | Check electrolyte level in battery, add distilled water if required. Maintain acid level below 5mm from the top case
6 | Check the terminals and apply petroleum jelly
7 | Note down battery voltage, should be DC 24 +/- 1V
8 | Reduce Fireline pressure to 4kg/cm2 before test running the Engine
9 | Test run the DG set for 5min and note down the paramater in DG log book
10 | Ensure no leakage in fuel, oil, water and exhaust line
11 | Clean the pump set completely
12 | Put the pump in Auto mode
13 | Check for fire line pressure
14 | Signature of Technician
15 | Signature Of Supervisor
16 | Oracle fire officer signature
Date Time | Abnormalities |  |  |  | Action Taken | [13 empty] | Status |  |  |  |  | Remarks
Signature Of Team Leader | [23 empty] | Signature of Manager

## Pump
PREVENTIVE MAINTENANCE CHECK LIST PUMPS
Sl.No | Location: | Type and Capacity: Primary/Secondary - HP |  |  |  | Date:
| Description | standard |  |  |  | Remarks
|  | Pump- | Pump- | Pump- | Pump-
1 | Check for any abnormal for the noise Level
2 | Check for any vibration in the system | [5 empty] | TAS/FMD/ENG/11/R0
3 | Check for any water leaks at the valves/glands
4 | Check for the Motor Overheating
5 | Check for any Lubrication oil/ leakages in the system
6 | Check for the Spider Conditions
7 | Check the Inlet/Outlet chilled water pressure
8 | Check for any Burning Smell & Sound From The Motor
9 | Check the voltage
10 | Check the Motor current
11 | Check the suction & discharge Pipe Lines Insulation Condition
12 | Check the condition of Base nuts, Bolts & tighten Motor
13 | Check the motor insulation resistance
14 | Check the electrical terminations at the Motor
15 | Check the electrical terminations at the panel
16 | Check the Panel
17 | Grease the Motor
18 | Clean the Strainer
Technician sign: |  | Team Leader Sign:
Supervisor sign:

## DB Panel
DB Panel Preventive Maintenance checklist
Sl.No | Location: |  |  |  | Date:
| Description | Check Report |  |  | Remarks
1 | Check the of physical condition
2 | Check for any abnormal noise/smell at the panels
3 | Check the voltage & current | RY= RN= | RY= RN= | RY= RN=
|  | YB= YN= | YB= YN= | YB= YN=
|  | BR= BN= | BR= BN= | BR= BN=
4 | Check the Lighting
5 | Check the Earthing
6 | Replace the indication Lamp /Meter at working condition
7 | Clean All the panels
8 | Check for Door Knobs / Screws & Door Operations
9 | Check Functioning the indication Lamp
10 | If Shutdown is available tighten all the cable connections
11 | Check the Earthing connections
12 | Check for MCB,MCCB Operations
14 | Check for MCB,MCCB & Cable Overheat
Technician sign: |  | Team Leader Sign:
Supervisor sign:

## LT Panel
LT PANEL PREVENTIVE MAINTENANCE CHECK LIST
Sl.No | Location: |  | Date:
| Description | Actual | Remarks
1 | Clean the Panels With Blower
2 | Check the Electrical terminals tightness of Panel
3 | Check the physical condition of Panel
4 | Check the any abnormal noise of Panel
5 | Check the voltage & current | RY= RN=
YB= YN=
BR= BN=
6 | Check the Earthing
7 | Check for Door Knobs / Screws & Door Operations
8 | Check Functioning the indication Lamp
9 | Check for MCB/ACB,Operations
10 | Check The Earth Pit Conditions, If Required Pour the Water
11 | Check For The Earth Leakage
12 | Check The Ammeter Condition
13 | Check The Voltmeter Condition
14 | Check The Energy Meter Condition
Technician sign: |  | Team Leader Sign:
Supervisor sign:

## Lift Panel
LIFT PANEL PREVENTIVE MAINTENANCE CHECK LIST
Sl.No | Location: |  | Date:
| Description | Check Report | Remarks
1 | Clean the Panels With Blower
2 | Check the Electrical terminals tightness of Panel
3 | Check the physical condition of Panel
4 | Check the any abnormal noise of Panel
5 | Check the voltage & current | RY= RN=
YB= YN=
BR= BN=
6 | Check the Earthing
7 | Replace the indication Lamp /Meter at working condition
8 | Check for Door Knobs / Screws & Door Operations
9 | Check Functioning the indication Lamp
10 | Check for MCB,MCCB,ACB Operations
11 | Check For The Earth Leakage
12 | Check The Ammeter Condition
13 | Check The Voltmeter Condition
Technician sign: |  | Team Leader Sign:
Supervisor sign:

## Chiller Panel
CHILLER PANEL PREVENTIVE MAINTENANCE CHECK LIST
Sl.No | Location: |  | Date:
| Description | Check Report | Remarks
1 | Clean the Panels With Blower
2 | Check the Electrical terminals tightness of Panel
3 | Check the physical condition of Panel
4 | Check the any abnormal noise of Panel
5 | Check the voltage & current | RY= RN=
YB= YN=
BR= BN=
6 | Check the Earthing |  |  | TAS/FMD/ENG/14/R0
7 | Replace the indication Lamp /Meter at working condition
8 | Check for Door Knobs / Screws & Door Operations
9 | Check Functioning the indication Lamp
10 | Check for MCB,MCCB,ACB Operations
11 | Apply Petroleum Jelly on Contact Points & Terminal Points
12 | Check The Gap B/ W Moving & Stationary Contacts
13 | Check The Earth Pit Conditions, If Required Pour the Water
14 | Check For The Earth Leakage
15 | Check The Ammeter Condition
16 | Check The Voltmeter Condition
Technician sign: |  | Team Leader Sign:
Supervisor sign:

## Street light
Street light Preventive Maintenance checklist
Location : | [7 empty] | Date:
Sl.No | Description | standard | Pole - | Pole - | Pole - | Pole - | Pole - | Remarks
|  |  | Actual | Actual | Actual | Actual | Actual
1 | Check The Lamps | Bright
2 | clean the reflector&fitting | Clean
3 | Check The Terminal Connectors | Should be Tight
4 | Check The Earth wire Connections | Should be Tight
5 | Check The Supply | 230 Volts
6 | Check The Capacitor | Good
7 | Check FRP box condition | Good
8 | Check the ballast condition | No Heat orNoise
9 | Check the condition of MCB | No Heat
Technician sign: | [7 empty] | Team Leader Sign:
Supervisor sign:

## Inverter
INVERTER CHECK LIST
UPS RATINGS : | [15 empty] | DATE :
TIME | OUTPUT VOLTAGE |  |  | OUTPUT CURRENT |  |  |  | % OF LOAD |  |  | KW |  |  | FREQUENCY |  | BATTERY |  |  | TEMP | TECH
| RY | YB | BR | R | Y | B | N | R | Y | B | R | Y | B | Invertor | Bypass | Voltage | Amps | % of Ch | In 0C | SIGN
8.00AM
10.00AM
12.00PM
14.00PM
16.00PM
18.00PM
20.00PM
22.00PM
00.00AM
02.00AM
04.00AM
06.00AM
Remarks :
Supervisor Sign : | [16 empty] | Team Leader Sign :

## FCU Unit
FCU PREVENTIVE MAINTENANCE CHECK LIST
Location: Capacity: |  | Date: |  | Remarks
Sl.No | Description | Standard | Actual
Indoor Unit
1 | Check the cleanliness of the filter | Clean |  |  | TAS/FMD/ENG/19/R0
2 | Check for any abnormal vibration in the FCU Unit. | Normal
3 | Check for any abnormal noise in the fan motor | Normal
4 | Check the room temperature | 220 - 230C
5 | Check the thermostat at working condition | working
6 | Check the current taken by the motor
7 | Check for any leakage of Refrigerant | No leakage
8 | Check the Electrical terminals tightness of the motor at the DB | Tight
Technician sign: |  | Team Leader Sign:
Supervisor sign:

## Split AC
SPLIT A/C PREVENTIVE MAINTENANCE CHECK LIST
Location: Capacity: |  | Date: |  | Remarks
Sl.No | Description | Standard | Actual
Indoor Unit
1 | Check the cleanliness of the Air filter | Clean
2 | Check for any abnormal vibration in the Split A/c | Normal
3 | Check for any abnormal noise in the fan motor | Normal
4 | Check the room temperature | 220 - 230C
5 | Check the remote control at working condition | working
Outdoor unit
6 | Check the current taken by the motor
7 | Check the motor winding resistance
8 | Check the motor insulation resistance
9 | Check for any leakage of Refrigerant | No leakage
10 | Check the Electrical terminals tightness of the motor at the DB | Tight
11 | Clean the outdoor unit | Clean
Technician sign: |  | Team Leader Sign:
Supervisor sign:

## DG PM
DG PREVENTIVE MAINTENANCE CHECK LIST
| Location: Capacity : |  |  | Date: |  |  | BATTERY CHECK REPORT
Sl no. | Descriptions | Standard | Check report
|  |  | DG- | DG- |  | DG-
1 | Check battery voltage, if necessary add electrolyte | 24-30V |  |  | CELL NO |  | Battery No 1 |  | Battery No 2
2 | Check the specific gravity of battery | 1.150 to 1.250 |  |  |  | Cell No | Sp Gravity | voltage | Sp Gravity | voltage
3 | To be check Lub oil level | High and Low |  |  | 1 | 1
4 | Cleaning of DG to be done | Clean |  |  | 2 | 2
5 | Check the Coolant Level | Full |  |  | 3 | 3
6 | Check the fan motor condition | Normal |  |  | 4 | 4
7 | Check the Belt condition | Tight |  |  | 5 | 5
8 | Check the Air Filter condition | Clean |  |  | 6 | 6
9 | Check the engine oil leakage and arrest if any | No Leakage |  |  |  | DG-
10 | Check for any abnormal for the noise | Normal |  |  | CELL NO |  | Battery No 1 |  | Battery No 2
11 | Drain water in the water separator | Up to Level |  |  |  | Cell No | Sp Gravity | voltage | Sp Gravity | voltage
12 | Check the diesel level in Tank | Above 70% |  |  | 1 | 1
13 | Take the trail run of the engine |  |  |  | 2 | 2
14 | Check the RPM of the engine | 1500 to 1550rpm |  |  | 3 | 3
15 | Check the water temperature | 40 to 60'c |  |  | 4 | 4
16 | Engine Oil Pressure |  |  |  | 5 | 5
17 | Check for all indication lamp at working condition | Glowing |  |  | 6 | 6
Remarks:
Technician sign: |  | Team Leader Sign:
Supervisor sign:
c

## Camera check list
CAMERA CHECK LIST
Legend
F | Functioning normally, check was performed
OL | Off Line
M | Malfunctioning
Camera | Location | TYPE | Camera Functionality |  |  | Remarks
|  |  | 1st Shift | 2nd Shift | 3rd Shift
CCTV Operator Name:
Team Leader Sign:

## Air Cooled Daily
AIR COOLED CHILLER -HVAC CONFORMANCE SHEET-DAILY
Date:- |  | Chiller No & Capacity:- | [5 empty] | Location:
Hrs | Water |  |  |  | Compression
Time | Temp |  | Pressure |  | Suction Pressure | DischargePressure | Set Point | Voltage | Current | Ambient Temp | Tech Sign
| IN-LET | OUTLET | IN-LET | OUTLET | KPA/PSIG | KPA/PSIG | Celcies | Input | Amps
Remarks:
Status | [5 empty] | Defects
[5 empty] | 1 | Vibration in Temp
[5 empty] | 2 | Water Flow sensors
[5 empty] | 3 | Electrical Circuit Problem
[5 empty] | 4 | Gas leakage
[5 empty] | 5 | Bearings
[5 empty] | 6 | Chiller Motar
[5 empty] | 7 | Compressor
[5 empty] | 8 | Others (Specify)
Checked By: | [7 empty] | Supervisor:
Sign: | [7 empty] | Sign:
Name: | [7 empty] | Name:

## NCCA report
NC/CA REPORT
TAS/FMD/ENG/22/R0
NC# 01 |  | DATE: 30th Apr-19
NATURE OF COMPLAINT:- EB TO DG Change Over issue @ Brigde Nalapad Center | CUSTOMER COMPLAINT / INTERNAL ISSUE
CUSTOMER/PROJECT | Nalapad Brigade Center
Description of Non Conformance: During EB power fail EB to DG Changeover panel issue
Root Cause Anaysis of NC:-(Why-Why Analysis):- Changeover panel contractor NO failure.
CORRECTIVE ACTION PROPOSED |  |  | DUE DATE
We have reset all the alaram and start the operation on manual mode |  |  | 30th Apr-19
REVIEWED BY Mahendra
AND DATE 30th Apr-19
COMMENTS ON CORRECTIVE ACTIONS ARE IMPLEMENTED:- We have Replaced with New contractor and working normal
PREPARED BY:- Mahendra |  |  |  | VERIFIED BY Mahendra
APPROVED BY Suresh Murthy